## Autosampler PLC Modbus Map
AUTOSAMPLER PLC MODBUS TABLE
Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | Modbus Address | Bit | Min Range | Max Range | Low Alarm | High Alarm | High High Alarm | Eng Unit | STATUS 0 | STATUS 1 | Comments | Alarm Comments
ANALYZER HOLDING REGISTERS
Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | Modbus Address | Bit | Min Range | Max Range | Low Alarm | High Alarm | High High Alarm | Eng Unit | STATUS 0 | STATUS 1 | Comments | Alarm Comments
| Stream_1_Panel_Watchdog | Panel PLC Watchdog | INT | READ | 40001 | N/A | 0 | 59 | N/A | N/A | N/A | N/A | N/A | N/A
| STREAM_1_Temp_Real | Cell Temperature | REAL | READ | 40002 | N/A | -20 | 80 | N/A | N/A | N/A | Deg. C | N/A | N/A
| STREAM_1_Pressure_Real | Cell Pressure | REAL | READ | 40004 | N/A | 0 | 10200 | N/A | N/A | N/A | kPag | N/A | N/A
| STREAM_1_Cyl_A_Status | Cylinder A Status | INT | READ | 40006 | N/A | 0 | 4 | N/A | N/A | N/A | N/A | N/A | N/A | STREAM 1 0=REMOVED 1=READY 2=FILL IN PROGRESS 3=FULL 4=ALARM
| STREAM_1_Cyl_B_Status | Cylinder B Status | INT | READ | 40007 | N/A | 0 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
|  | Panel Warning Integer - High Temperature | INT | READ | 40008 | 0 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI
|  | Panel Warning Integer - Low Temperature | INT | READ | 40008 | 1 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI
|  | Panel Warning Integer - High Pressure | INT | READ | 40008 | 2 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI
|  | Panel Warning Integer - Low Pressure | INT | READ | 40008 | 3 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI
|  | Panel Warning Integer - Fill Failed, Second Try | INT | READ | 40008 | 4 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal |  | First fill failure has triggered a second attempt
|  | Panel Fault Integer - Temperature transmitter fault | INT | READ | 40009 | 0 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Loss of RTD signal
|  | Panel Fault Integer - Pressure transmitter fault | INT | READ | 40009 | 1 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Loss of 4-20 mA signal
|  | Panel Fault Integer - Fill Failed | INT | READ | 40009 | 2 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Initial fill attempt failure | Reset Cylinder to clear
|  | Panel Fault Integer - Second Fill Failed | INT | READ | 40009 | 3 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Second fill attempt failure
|  | Panel Fault Integer - No Cylinders Available | INT | READ | 40009 | 4 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | No cylinders Enabled on the panel | Add cylinder(s) to clear
|  | Panel Fault Integer - Maintenance Switch | INT | READ | 40009 | 5 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Panel has been placed into Maintenance Hold mode | Cylinder fill requests supressed
|  | Cylinder A Warning Integer - Fill Too Short | INT | READ | 40010 | 0 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI (60 to 120 sec)
|  | Cylinder A Warning Integer - Fill Too Long | INT | READ | 40010 | 1 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI (120 to 500 sec)
|  | Cylinder A Warning Integer - Recharge Cylinder | INT | READ | 40010 | 2 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Cylinder is ready to recharge
|  | Cylinder A Fault Integer - Fill Failed To Start | INT | READ | 40011 | 1 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed to start
|  | Cylinder A Fault Integer - Empty Sensor Fault | INT | READ | 40011 | 2 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed - Pisotn moved durring purge cycle
|  | Cylinder A Fault Integer - Maintenance Bypass | INT | READ | 40011 | 4 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed - Maintenace mode selected during a fill
|  | Cylinder B Warning Integer - Fill Too Short | INT | READ | 40012 | 0 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI (60 to 120 sec)
|  | Cylinder B Warning Integer - Fill Too Long | INT | READ | 40012 | 1 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Set at HMI (120 to 500 sec)
|  | Cylinder B Warning Integer - Recharge Cylinder | INT | READ | 40012 | 2 | 0 | 1 | N/A | N/A | N/A | N/A | Warning | Normal | Cylinder is ready to recharge
|  | Cylinder B Fault Integer - Fill Failed To Start | INT | READ | 40013 | 1 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed to start
|  | Cylinder B Fault Integer - Empty Sensor Fault | INT | READ | 40013 | 2 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed - Piston moved durring purge cycle
|  | Cylinder B Fault Integer - Maintenance Bypass | INT | READ | 40013 | 4 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed - Maintenace mode selected during a fill
|  | VCON Normal | INT | READ | 40014 | 4 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed - Maintenace mode selected during a fill
|  | VCON Get Ready | INT | READ | 40015 | 4 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed - Maintenace mode selected during a fill
|  | VCON Sampling | INT | READ | 40016 | 4 | 0 | 1 | N/A | N/A | N/A | N/A | Fault | Normal | Fill Failed - Maintenace mode selected during a fill
| SCADA_YEAR | Sample Trigger | INT | WRITE | 40020 | N/A | 0 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | Autosample request from VCON
| SCADA_YEAR | VCON Clock Year | INT | WRITE | 40021 | N/A | 2016 | 2116 | N/A | N/A | N/A | YR | N/A | N/A | Time Sync for HMI
| SCADA_MONTH | VCON Clock Month | INT | WRITE | 40022 | N/A | 1 | 12 | N/A | N/A | N/A | MON | N/A | N/A | Time Sync for HMI
| SCADA_DAY | VCON Clock Day | INT | WRITE | 40023 | N/A | 1 | 31 | N/A | N/A | N/A | DAY | N/A | N/A | Time Sync for HMI
| SCADA_HOUR | VCON Clock Hour | INT | WRITE | 40024 | N/A | 0 | 24 | N/A | N/A | N/A | HR | N/A | N/A | Time Sync for HMI
| SCADA_MINUTE | VCON Clock Minute | INT | WRITE | 40025 | N/A | 0 | 60 | N/A | N/A | N/A | MIN | N/A | N/A | Time Sync for HMI
| SCADA_SECOND | VCON Clock Second | INT | WRITE | 40026 | N/A | 0 | 60 | N/A | N/A | N/A | SEC | N/A | N/A | Time Sync for HMI
| STREAM_1_BarCode_Reg_1 | VCON BARCODE Segment 1 | INT | WRITE | 40027 | N/A | 0 | 65535 | N/A | N/A | N/A | N/A | N/A | N/A
| STREAM_1_BarCode_Reg_2 | VCON BARCODE Segment 2 | INT | WRITE | 40028 | N/A | 0 | 65535 | N/A | N/A | N/A | N/A | N/A | N/A
| STREAM_1_BarCode_Reg_3 | VCON BARCODE Segment 3 | INT | WRITE | 40029 | N/A | 0 | 65535 | N/A | N/A | N/A | N/A | N/A | N/A
| STREAM_1_C1_Real | C1 - Methane | REAL | WRITE | 40030 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_C2_Real | C2 - Ethane | REAL | WRITE | 40032 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_C3_Real | C3 - Propane | REAL | WRITE | 40034 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_iC4_Real | iC4 - isoButane | REAL | WRITE | 40036 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_nC4_Real | nC4 - normal Butane | REAL | WRITE | 40038 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_iC5_Real | iC5 - isoPentane | REAL | WRITE | 40040 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_nC5_Real | nC5 - normal Pentane | REAL | WRITE | 40042 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_C6plus_Real | C6 plus - Hexane plus | REAL | WRITE | 40044 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A
| STREAM_1_C6plus_Real | VCON Ready | REAL | WRITE | 40045 | N/A | 0 | 100 | N/A | N/A | N/A | VOL% | N/A | N/A